## Sheet1
Color code
Same parameters
Same functions can be fulfilled by different parameters
Functions that FC280 does not have
VLT 2800 |  |  | Midi Drive FC280 |  | Note | FC280 new function parameters
001 Language |  | 0-01 Language |  |  |  | 0-06 GridType
002 Local/remote control |  | Fulfilled by LCP key |  |  |  | 0-07 Auto DC Braking IT
003 Local reference
004 Active Setup |  | 0-10 Active Set-up |  |  |  | 0-30 Custom Readout Unit
005 Programming Setup |  | 0-11 Programming Set-up
006 Copying of Setups |  | 0-51 Set-up Copy |  |  |  | 1-10 Motor Construction
007 LCP copy |  | 0-50 LCP Copy
008 Display scaling of motor frequency |  | 0-3* Customer readout
009 Display line 2 |  | (0-23) Display Line 2 Large |  |  |  | 1-14 Damping Gain
010 Display line 1.1 |  | (0-20) Display Line 1.1 Small |  |  |  | 1-15 Low Speed Filter Time Const
011 Display line 1.2 |  | (0-21) Display Line 1.2 Small |  |  |  | 1-16 High Speed Filter Time Const
012 Display line 1.3 |  | (0-22) Display Line 1.3 Small |  |  |  | 1-17 Voltage filter time const
013 Local control/configuration |  |  |  | Reference can not be changed by LCP in Remote mode for FC280
014 Local stop |  | Similar feature as 0-4* LCP keypad |  |  |  | 1-29 Automatic Motor Adaption (AMA)
015 Local jog 2 | [5 empty] | 1-42 Motor Cable Length
016 Local reversing
017 Local reset of trip | [5 empty] | 2-06 Parking Current
018 Lock for data change |  | 0-60 Main Menu Password |  |  |  | 2-07 Parking Time
019 Operating state at power up |  | 0-04 Operating State at Power-up
020 Hand Operation |  | 0-4* LCP Keypad |  |  |  | 7-1* Torque PID Ctrl.
024 Userdefined Quick Menu |  |  |  | FC280 does not have this feature. But by using application selection,some application can be easily set.
025 Quick Menu Set-up | [5 empty] | 13-** Smart Logic
100 Configuration |  | 1-00 Configuration Mode
101 Torque characteristics |  | 1-03 Torque Characteristics
102 Motor power |  | 1-20 Motor Power |  |  |  | 14-41 AEO Minimum Magnetisation
103 Motor voltage |  | 1-22 Motor Voltage
104 Motor frequency |  | 1-23 Motor Frequency |  |  |  | 22-6* Broken Belt Detection
105 Motor current |  | 1-24 Motor Current
106 Rated motor speed |  | 1-25 Motor Nominal Speed |  |  |  | 24-10 Drive Bypass Function
107 Automatic Motor Tuning, AMT |  | 1-29 Automatic Motor Adaption (AMA) |  |  |  | 24-11 Drive Bypass Delay Time
108 Stator Resistance RS |  | 1-30 Stator Resistance (Rs)
109 Stator Reactance XS |  | 1-35 Main Reactance |  |  |  | 30-2* Adv. Start Adjust
117 Resonance damping off |  | 1-64 Resonance Dampening
119 High Start Torque |  | 1-78/1-79 Compressor Start |  |  |  | 33-** Motion Control function/Positioning
120 Start Delay |  | 1-71 Start delay
121 Start Function |  | 1-72 Start function
122 Function at Stop |  | 1-80 Function at stop
123 Min. Frequency for Activation of Function at Stop |  | 1-82 Min speed for function at Stop [Hz]
126 DC Brake Time |  | 2-02 DC Braking Time
127 DC brake cut-in frequency |  | 2-04 DC Brake Cut In Speed
132 DC braking voltage |  | 2-01 DC Brake Current
128 Motor thermal protection |  | 1-90 Motor Thermal Protection
130 Start Frequency |  | 1-75 Start Speed [Hz]
131 Initial Voltage |  | (1-76) Start Current
132 DC braking voltage |  | 2-01 DC brake current
133 Start voltage |  | (1-55) U/f Characteristic - U
134 Load compensation |  | 1-60/1-61 Low/High speed load compensation
135 U/f ratio |  | 1-55/1-56 U/f Characteristic
136 Slip compensation |  | 1-62 Slip Compensation
137 DC holding voltage |  | 2-00 DC Hold/Motor Preheat Current
138 Brake cut out frequency |  | 2-20 Release Brake Current |  | VLT 2800 release brake based on output frequency. FC280 base on current
139 Brake cut in frequency |  | 2-22 Activate Brake Speed [Hz]
140 Current, Minimum Value |  | 2-20 Release Brake Current
142 Leakage Reactance XL |  | 1-33 Stator Leakage Reactance (X1)
143 Internal Fan Control |  | 14-52 Fan control
144 Gain AC Brake |  | 1-88 AC brake Gain
146 Reset Voltage Vector
200 Rotation direction |  | 4-10 Motor Speed Direction
201 Min. output frequency (fMIN)
202 Max. output frequency |  | 4-19 Max Output Frequency
203 Reference/feedback range |  | 3-00 Reference range |  | Ref/feedback range: Min-Max, -Max- +Max
204 Minimum reference |  | 3-02 Minimum Reference
205 Maximum reference |  | 3-03 Maximum Reference
206 Ramp Type |  | 3-04 Ramp 1 Type
207 Ramp-up time 1 |  | 3-41 Ramp 1 Ramp up Time
208 Ramp-down time 1 |  | 3-42 Ramp 1 Ramp Down Time
209 Ramp-up time 2 |  | 3-51 Ramp 2 Ramp up Time
210 Ramp-down time 2 |  | 3-52 Ramp 2 Ramp down Time
211 Jog ramp time |  | 3-80 Jog Ramp Time
212 Quick stop ramp-down time |  | 3-81 Quick Stop Ramp Time
213 Jog frequency |  | 3-11 Jog Speed [Hz]
214 Reference function |  | 3-04 Reference Function
215 Preset reference 1 |  | 3-10 Preset Reference
216 Preset reference 2
217 Preset reference 3
218 Preset reference 4
219 Catch up/slow down value |  | 3-12 Catch up/slow Down Value
221 Current limit for motor mode |  | 4-18 Current Limit
223 Warning, Low Current, ILOW |  | 4-50 Warning Current Low
224 Warning: High Current, IHIGH |  | 4-51 Warning Current high
225 Warning: Low Frequency, fLOW |  | 4-40 Warning Freq. Low
226 Warning: High Frequency fHIGH |  | 4-41 Warning Freq. High
227 Warning: Low Feedback, FBLOW |  | 4-56 Warning Feedback Low
228 Warning: High Feedback, FBHIGH |  | 4-57 warning Feedback High
229 Frequency bypass bandwidth
230 Frequency bypass 1 |  | 4-6* Speed Bypass
231 Frequency bypass 2
317 Time out |  | 6-00 Live Zero Timeout Time
318 Function after time out |  | 6-01 Live Zero Timeout Function
323 X102 relay function |  | 5-40 Function Relay
327 Pulse reference/feedback, max. |  | 5-53 Term. 29 High Ref./Feedb. Value
328 Maximum Pulse 29 |  | 5-51 Term. 29 High Frequency
302 Terminal 18 Digital Input |  | 5-10 Terminal 18 Digital Input
303 Terminal 19 Digital input |  | 5-11 Terminal 19 Digital Input
304 Terminal 27 Digital Input |  | 5-13 Terminal 27 Digital Input
305 Terminal 29 Digital Input |  | 5-14 Terminal 29 Digital Input
307 Terminal 33 Digital Input |  | 5-15 Terminal 33 Digtal input
308 Terminal 53, Analog Input Voltage |  |  |  | 53 is signal source choosen under each function
309 Terminal 53 Min. Scaling |  | 6-10 Terminal 53 Low Voltage
310 Terminal 53 Max. Scaling |  | 6-11 Terminal 53 High Voltage
314 Terminal 60 Analog Input Current |  |  |  | 60 is signal source choosen under each function
315 Terminal 60 Min. Scaling |  | 6-22 Terminal 54 Low Current
316 Terminal 60 Max. Scaling |  | 6-23 Terminal 54 High Current
319 Analog output 42 |  | 6-91 Terminal 42 Analog Output
341 Digital/Pulse Output Terminal 46 |  | 5-60 pulse output/5-30 Digital Output 27
342 Terminal 46, max. Pulse Scaling |  | (5-62) Pulse Output Max Freq 27
343 Precise Stop Function |  | (1-83) Precise Stop Function
344 Counter Value |  | (1-84) Precise Stop Counter Value
349 Speed Comp Delay |  | (1-85) Precise Stop Speed Compensation Delay
400 Brake function |  | 2-10 Brake Function
405 Reset function |  | 14-20 Reset Mode
406 Auotomatic Restart Time |  | 14-21 Automatic Restart Time
409 Trip Delay Overcurrent, ILIM |  | 14-24 Trip Delay at Current Limit
411 Switching frequency |  | 14-01 Switching Frequency
412 Variable switching frequency |  | (14-55) Output Filter
413 Overmodulation function |  | 14-03 Overmodulation
414 Minimum feedback |  | 6-14 low feedback 53/6-24 low feedback 54
415 Maximum feedback |  | 6-14 High feedback 53/6-24 High feedback 54
416 Process unit |  | 3-01 Reference/Feedback Unit |  | Can not define in FC280
417 Speed PID Proportional Gain |  | (7-02) Speed PID Proportional Gain
418 Speed PID Integral Time |  | (7-03) Speed PID Integral Time
419 Speed PID Differential Time |  | (7-04) Speed PID Differentiation Time
420 Speed PID D-Gain Limit |  | (7-05) Speed PID Diff. Gain Limit
421 Speed PID Lowpass Filter Time |  | (7-06) Speed PID Lowpass Filter Time
423 U1 Voltage |  | 1-55 U/f Characteristic - U/ 1-56 U/f Characteristic - F
424 F1 Frequency
425 U2 Voltage
426 F2 Frequency
427 U3 Voltage
428 F3 Frequency
437 Process PID normal/inverse ctrl. |  | 7-30 Process PID Normal/ Inverse Control
438 Process PID anti windup |  | 7-31 Process PID Anti Windup
439 Process PID start frequency |  | 7-32 Process PID Start Speed
440 Process PID proportional gain |  | 7-33 Process PID Proportional Gain
441 Process PID integral time |  | 7-34 Process PID Integral Time
442 Process PID differentation time |  | 7-35 Process PID Differentiation Time
443 Process PID different. gain |  | 7-36 Process PID Diff. Gain Limit
444 Process PID lowpass filter time |  | 6-16/6-26 terminal 53/54 filter time constant
445 Flying start |  | 1-73 Flying Start
451 Speed PID Feedforward Factor |  | 7-08 Speed PID Feed Forward Factor
452 Controller Range
455 Monitor frequency range
456 Brake Voltage Reduce |  | 2-14 Brake voltage reduce
457 phase lose |  | 14-12 Function at mains Imbalance
461 Feedback conversion |  | 7-6* Feedback conversion
462 Enhanced Sleep Mode Timer |  | 22-4*Sleep mode
463 Boost Setpoint
464 Wakeup Pressure
465 Minimum Pump Frequency |  |  |  | Dry pump feature
466 Maximum Pump Frequency
467 Minimum Pump Power
468 Maximum Pump Power
469 No Flow Power Compensation
470 Dry Run Time Out
471 Dry Run Interlock Timer
484 Initial Ramp |  |  |  | Anti Water Hammer function
485 Fill Rate
486 Filled Setpoint
500 Bus address |  | 8-31 Address
501 Baudrate |  | 8-32 Baud Rate
502 Coasting |  | 8-50 Coasting Select
503 Quick-stop |  | 8-51 Quick Stop Select
504 DC-brake |  | 8-52 DC Brake Select
505 Start |  | 8-53 Start Select
506 Reversing |  | 8-54 Reversing Select
507 Selection of setup |  | 8-55 Set-up Select
508 Selection of speed |  | 8-56 Preset Reference Select
509 Bus jog |  | 3-11 Jog speed |  | Jog function controlled by Bus
510 Bus jog |  | 3-11 Jog speed
512 Telegram profile |  | 8-30 Protocol
513 Bus time interval |  | 8-03 Control Timeout Time
514 Bus time interval function |  | 8-04 Control Timeout Function
515 Data read-out: Reference |  | 16-02 Reference [%]
516 Data read-out: Refer. unit |  | 16-01 Reference [Unit]
517 Data read-out: Feedback |  | 16-52 Feedback[Unit]
518 Data read-out: Frequency |  | 16-15 Frequency [%]
519 Data read-out: Frequency x scale |  | 16-13 Frequency
520 Data read-out: Current |  | 16-14 Motor Current
521 Data read-out: Torque % |  | 16-22 Torque [%]
522 Data read-out: Power kW |  | 16-10 Power [kW]
523 Data read-out: Power hp |  | 16-11 Power [hp]
524 Data read-out: Motor voltage |  | 16-12 Motor Voltage
525 Data read-out: DC link voltage |  | 16-30 DC Link Voltage
526 Data readout: Motor thermal load |  | 16-18 Motor Thermal
527 Data read-out: FC therm |  | 16-35 Inverter Thermal |  | Show the percentage load on the inverter
528 Data read-out: Digital input |  | 16-60 Digital input
529 Data readout: Analog input, term. 53 |  | 16-62 Analog Input 53
531 Data readout: Analog input, term. 60 |  | 16-64 Analog Input AI54
532 Data readout: Pulse reference |  | 16-68 Pulse Input 33 [Hz]
533 Data read-out: External reference |  | 16-50 External Reference
534 Data read-out: Status word, binary |  | 16-03 Status Word
537 Data read-out: FC temperature |  | 16-34 Heatsink Temp.
538 Data read-out: Alarm word |  | 16-90 Alarm Word
539 Data read-out: Control word |  | 16-00 Control Word
540 Data read-out: Warning word |  | 16-92 Warning Word
541 Data read-out: Warning word |  | 16-93 Warning Word 2
600 Operating data: Operating hours |  | 15-00 Operating Hours
601 Operating data: Hours run |  | 15-01 Running Hours
603 Operating data: Number of power-up's |  | 15-03 Power Up's
604 Operating data: Number of overtemp. |  | 15-04 Over Temp's
605 Operating data: Number of overvoltages |  | 15-05 Over Volt's
615 Fault log, read-out: Error code |  | 15-30 Alarm Log: Error Code
616 Fault log, read-out: Time |  | 15-30 Alarm Log: Error Code
617 Fault log, read-out: Value |  | 15-31 Internal Fault Reason
618 Reset of kWh counter |  | (15-06) Reset kWh Counter
619 Reset of hours-run counter |  | 15-07 Reset Running Hours Counter
620 Operation mode 0 |  | 15-** Drive Information |  | Product information
621 Nameplate: FC motor type
624 Nameplate: Software version no.
625 LCP version Depends on unit
626 Nameplate: Database identification no.
628 Nameplate: Application option type
630 Nameplate: Communication option type
632 BMC software identification
634 Unit identification for communication
635 Software part No.
640 Software version
641 BMC software identification
642 Power card identification
700 Wobble Mode |  |  |  | Wobble function
702 Delta Frequency
703 Jump Frequency
704 Jump time
705 Wobble Time
706 Wobble Ratio
707 Random Function
708 Random Max
709 Random Min